MANUAL

Program sinsyn.m and model singen.mdl collectively used to simulate single machine infinite bus system. It can be used to simulate the  following disturbances:

1) Step change in Tm

2) Step change in Vref

3) Step change in  Eb

4) Step change in reference value of omega

5) Step change in infinite bus angle

Following component models are used in the program and model.

GENERATOR MODEL

Generator is represented by 1.1 model.

Input file:machine.dat

Data to be entered:

Ra

Xq

Xd

X1q

X1d

T1do

T1qo

H

D

f

EXCITATION SYSTEM:

User can opt for any type of Excitation system among IEEE Type-1 Excitation system and Static Excitation system, or excitation system can be excluded. Block diagram for both Excitation system are shown below.

Input file for IEEE type-1 Excitation system: excieee1.dat

Data to be entered:

A

B

TR

TA

TF

TE

KA

KF

KE

Vrmax

Vrmin

Input file for Static Excitation system: excst1.dat

Data to be entered:

TC

TB

KA

TA

Efdmax

Efdmin

IEEE Type-1 Excitation system

vg                Vref                 vrmax                   Efd

1

1+TR

KA

1+sTA

1

KE+sTE

Vs         vrmin

SE=f(EFD)

sKF

1+sTF

Static Excitation system

Efdmax

1+sTC

1+sTB

KA

1+sTA

Vref                               Efd

-vg

vs

Efdmin

vref  - AVR reference voltage

vg    - Generator terminal voltage

vs  -PSS output voltage

POWER SYSTEM STABILIZER

User can opt for power system stabilizer or it can be excluded. Block diagram of PSS is shown below.

Input file: pss.dat

Data to be entered:

Ks

Tw

T1

T2

T3

T4

Vsmax

Vsmin

vsmax

sTW

1+sTW

KS(1+sT1)(1+sT3)

(1+sT2)(1+sT4)

Sm                                           vs

(slip)                                   vsmin

GOVERNOR-TURBINE

User can opt for either Hydro governor-turbine model or steam governor-turbine model. Governor-turbine can also be excluded. Block diagram for Hydro governor-turbine and steam governor-turbine are given below.

Input file for hydro governor-turbine: hydrogov.dat

Data to be entered:

Tr

Tg

Tp

Delta

Sigma

T2

Tw

Pmax

Pmin

Input file for steam governor-turbine: steamgov.dat

Data to be entered:

Tch

Trh

Tco

Fhp

Fip

Flp

T1

T2

T3

Sigma

Pup

Pdown

Pmax

Pmin

SPEED GOVERNOR FOR HYDROTURBINE

K(1+sT2)

(1+sT1)(1+sT3)

Pmax

__

                             Pgv

Pmin

HYDROTURBINE MODEL

1-sTW

1+0.5sTW

Pgv                        Pm

SPEED GOVERNOR FOR STEAM TURBINE

_                                      .

                                      Pup   Pmax     Pgv

K(1+sT2)

(1+sT1)

1

T3

1

s

.

Pdown  Pmin

STEAM TURBINE MODEL

1

1+sTch

1

1+sTrh

1

1+sTco

Pgv                                                        Pm

Fhp

Fip

Flp

NETWORK

Vt=IaY11+h12Eb1Y11=zR+jzIh12=h1+jh2Network is represented by h and z parameters at generator terminal. That is

Where Vt is the generator terminal voltage, Eb is the infinite bus voltage, Y11 is the short circuit self admittance of the network, measured at the generator terminals and h12 is the open circuit voltage gain. Value of h1,h2,zR and zI will have to be entered in the MATLAB program sinsyn.m

Simulink model

User is prompted to select the type of disturbance and to decide presence of excitation system, governor turbine and pss by clicking on the self explanatory blocks. User can obtain help regarding entering data by clicking on help button provided. Output plots can be observed in the scopes provided for different parameters.

Different data has to be entered in the input files created by user. All data files namely(machine.dat, hydrogov.dat, steamgov.dat, excieee1.dat, excst1.dat, pss.dat) program file(sinsyn.m) and model file(singen.mdl) has to be kept in same directory.

For running this program MATLAB command window has to be opened and sinsyn.m is typed in the command window. System can be simulated with singen.mdl model file after sinsyn.m is executed.

Initial value of different parameters can be viewed in MATLAB command window just by typing variable name of parameter. They are listed below.

Parameter                  Variable name

terminal voltage,angle       vg,thetao

Active and reactive power    pg,qg

Ia                           iao

Eq                           eqo

rotor angle						deltao

Id									ido

Iq                           iqo

Vd                           vdo

Vq								   vqo

Efd                          efdo

Eq1                                         eqo1

Ed1                          edo1

Tm                           tmo